## Sheet1
Sample loss calculation for default Wind / Commercial configuration in SAM
From Losses input page | x (%) | 1-x/100
Total wake losses | 1.1 | 0.989
Total availability losses | 5.5 | 0.945
Total electrical losses | 2.008 | 0.97992
Total turbine performance loss | 3.954 | 0.96046
Total environmental loss | 2.398 | 0.97602
Curtailment and operation strategies loss total | 2.803 | 0.97197
Sum | 17.763 | 16.5532 | The total loss should also include any losses on the Wind Farm or Grid Limits page.
100% - Sum | 82.237 | 83.4468 | For the default Wind / Commercial case those losses are zero, so I did not include them here.
From simulation results
Annual energy (kWh) | gross | 392981
| net | 327922
| net/gross | 0.83445