## V6 module ds inverter eff
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray | Tilt | 15
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tree 1 | 15m
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Inverter eff | 60%
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 36.7647 | 13.926 | 306.659 | 0.20196 | 0.061933 | 61.9333
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 149.949 | 19.5239 | 322.319 | 1.2641 | 0.40743 | 407.429
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.29 | 29.5282 | 318.785 | 3.9333 | 1.2539 | 1253.88
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.292 | 37.1503 | 309.843 | 5.4805 | 1.6981 | 1698.1
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 747.66 | 44.2054 | 300.676 | 6.7005 | 2.0147 | 2014.67
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.086 | 47.1814 | 296.623 | 7.5501 | 2.2395 | 2239.53
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 907.944 | 50.9522 | 291.524 | 8.0278 | 2.3403 | 2340.29
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.634 | 49.449 | 293.447 | 8.1384 | 2.3882 | 2388.19
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 889.818 | 50.4141 | 292.293 | 7.8313 | 2.289 | 2289.04
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 810.451 | 49.3621 | 293.829 | 7.1383 | 2.0974 | 2097.44
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 689.591 | 44.2879 | 300.508 | 6.0878 | 1.8294 | 1829.44
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.303 | 40.5189 | 304.959 | 4.8792 | 1.488 | 1487.95
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 309.057 | 33.0643 | 311.087 | 2.6613 | 0.82789 | 827.89
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 98.4647 | 24.8727 | 309.332 | 0.81544 | 0.25224 | 252.242
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.0856 | 22.9671 | 302.482 | 0.39595 | 0.11977 | 119.769
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.6165 | 20.361 | 299.496 | 0.24165 | 0.072374 | 72.3742
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.8847 | 18.4476 | 288.105 | 0 | 0.02526 | 25.2603
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is not an output in SAM, here is calculated based on SAM’s array voltage and power.

## V5 module ds shadows tree1 15m
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray | Tilt | 15
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 36.7647 | 13.926 | 306.659 | 0.20196 | 0.061933 | 61.9333
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 149.949 | 19.5239 | 322.319 | 1.2641 | 0.40743 | 407.429
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.29 | 29.5282 | 318.785 | 3.9333 | 1.2539 | 1253.88
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.292 | 37.1503 | 309.843 | 5.4805 | 1.6981 | 1698.1
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 747.66 | 44.2054 | 300.676 | 6.7005 | 2.0147 | 2014.67
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.086 | 47.1814 | 296.623 | 7.5501 | 2.2395 | 2239.53
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 907.944 | 50.9522 | 291.524 | 8.0278 | 2.3403 | 2340.29
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.634 | 49.449 | 293.447 | 8.1384 | 2.3882 | 2388.19
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 889.818 | 50.4141 | 292.293 | 7.8313 | 2.289 | 2289.04
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 810.451 | 49.3621 | 293.829 | 7.1383 | 2.0974 | 2097.44
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 689.591 | 44.2879 | 300.508 | 6.0878 | 1.8294 | 1829.44
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.303 | 40.5189 | 304.959 | 4.8792 | 1.488 | 1487.95
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 309.057 | 33.0643 | 311.087 | 2.6613 | 0.82789 | 827.89
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 98.4647 | 24.8727 | 309.332 | 0.81544 | 0.25224 | 252.242
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.0856 | 22.9671 | 302.482 | 0.39595 | 0.11977 | 119.769
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.6165 | 20.361 | 299.496 | 0.24165 | 0.072374 | 72.3742
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.8847 | 18.4476 | 288.105 | 0 | 0.02526 | 25.2603
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is not an output in SAM, here is calculated based on SAM’s array voltage and power.

## V4 V and P x 0.8
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray | Tilt | 15
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 36.857 | 13.9288 | 245.352 | 0.20248 | 0.049678 | 49.6785
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 150.134 | 19.5297 | 257.8512 | 1.2657 | 0.32636 | 326.3632
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.534 | 29.5355 | 255.02 | 3.9355 | 1.0036 | 1003.632
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.557 | 37.1585 | 247.8624 | 5.4829 | 1.359 | 1359.016
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 747.948 | 44.2144 | 240.5296 | 6.703 | 1.6123 | 1612.272
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.375 | 47.19 | 237.2896 | 7.5526 | 1.7922 | 1792.152
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 908.236 | 50.9611 | 233.208 | 8.0303 | 1.8727 | 1872.736
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.913 | 49.4568 | 234.7536 | 8.1406 | 1.911 | 1911.04
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 890.086 | 50.4218 | 233.8232 | 7.8337 | 1.8317 | 1831.704
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 810.712 | 49.3697 | 235.0552 | 7.1406 | 1.6784 | 1678.424
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 689.852 | 44.2955 | 240.3952 | 6.0902 | 1.464 | 1464.048
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.548 | 40.5262 | 243.96 | 4.8813 | 1.1908 | 1190.848
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 393.46 | 35.652 | 247.5808 | 3.3876 | 0.83871 | 838.712
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 108.017 | 25.1338 | 248.02 | 0.88653 | 0.21988 | 219.8776
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.2046 | 22.971 | 242.0104 | 0.39701 | 0.096081 | 96.0808
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.6902 | 20.3634 | 239.6264 | 0.2423 | 0.058061 | 58.0614
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.9166 | 18.4487 | 230.5128 | 0 | 0.020265 | 20.2652
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is not an output in SAM, here is calculated based on SAM’s array voltage and power.

## V4 module ds shadows inverter
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray | Tilt | 15
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 36.857 | 13.9288 | 306.69 | 0.20248 | 0.062098 | 62.0981
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 150.134 | 19.5297 | 322.314 | 1.2657 | 0.40795 | 407.954
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.534 | 29.5355 | 318.775 | 3.9355 | 1.2545 | 1254.54
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.557 | 37.1585 | 309.828 | 5.4829 | 1.6988 | 1698.77
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 747.948 | 44.2144 | 300.662 | 6.703 | 2.0153 | 2015.34
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.375 | 47.19 | 296.612 | 7.5526 | 2.2402 | 2240.19
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 908.236 | 50.9611 | 291.51 | 8.0303 | 2.3409 | 2340.92
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.913 | 49.4568 | 293.442 | 8.1406 | 2.3888 | 2388.8
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 890.086 | 50.4218 | 292.279 | 7.8337 | 2.2896 | 2289.63
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 810.712 | 49.3697 | 293.819 | 7.1406 | 2.098 | 2098.03
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 689.852 | 44.2955 | 300.494 | 6.0902 | 1.8301 | 1830.06
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.548 | 40.5262 | 304.95 | 4.8813 | 1.4886 | 1488.56
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 393.46 | 35.652 | 309.476 | 3.3876 | 1.0484 | 1048.39
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 108.017 | 25.1338 | 310.025 | 0.88653 | 0.27485 | 274.847
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.2046 | 22.971 | 302.513 | 0.39701 | 0.1201 | 120.101
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.6902 | 20.3634 | 299.533 | 0.2423 | 0.072577 | 72.5767
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.9166 | 18.4487 | 288.141 | 0 | 0.025331 | 25.3315
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is not an output in SAM, here is calculated based on SAM’s array voltage and power.

## V3 module ds shadows
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray | Tilt | 15
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 36.857 | 13.9288 | 306.69 | 0.20248 | 0.062098 | 62.0981
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 150.134 | 19.5297 | 322.314 | 1.2657 | 0.40795 | 407.954
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.534 | 29.5355 | 318.775 | 3.9355 | 1.2545 | 1254.54
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.557 | 37.1585 | 309.828 | 5.4829 | 1.6988 | 1698.77
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 747.948 | 44.2144 | 300.662 | 6.703 | 2.0153 | 2015.34
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.375 | 47.19 | 296.612 | 7.5526 | 2.2402 | 2240.19
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 908.236 | 50.9611 | 291.51 | 8.0303 | 2.3409 | 2340.92
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.913 | 49.4568 | 293.442 | 8.1406 | 2.3888 | 2388.8
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 890.086 | 50.4218 | 292.279 | 7.8337 | 2.2896 | 2289.63
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 810.712 | 49.3697 | 293.819 | 7.1406 | 2.098 | 2098.03
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 689.852 | 44.2955 | 300.494 | 6.0902 | 1.8301 | 1830.06
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.548 | 40.5262 | 304.95 | 4.8813 | 1.4886 | 1488.56
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 393.46 | 35.652 | 309.476 | 3.3876 | 1.0484 | 1048.39
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 108.017 | 25.1338 | 310.025 | 0.88653 | 0.27485 | 274.847
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.2046 | 22.971 | 302.513 | 0.39701 | 0.1201 | 120.101
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.6902 | 20.3634 | 299.533 | 0.2423 | 0.072577 | 72.5767
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.9166 | 18.4487 | 288.141 | 0 | 0.025331 | 25.3315
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is not an output in SAM, here is calculated based on SAM’s array voltage and power.

## V2 module ds shadows
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray | Tilt | 15.6
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 37.4909 | 13.946 | 306.857 | 0.20536 | 0.063017 | 63.0165
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 150.727 | 19.5481 | 322.336 | 1.2707 | 0.4096 | 409.6
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.942 | 29.5476 | 318.76 | 3.9392 | 1.2556 | 1255.65
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.998 | 37.1722 | 309.813 | 5.4868 | 1.6999 | 1699.89
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 748.429 | 44.2296 | 300.642 | 6.7072 | 2.0165 | 2016.47
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.857 | 47.2044 | 296.583 | 7.557 | 2.2413 | 2241.27
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 908.723 | 50.976 | 291.486 | 8.0346 | 2.342 | 2341.97
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.891 | 49.4561 | 293.442 | 8.1403 | 2.3887 | 2388.71
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 886.436 | 50.3156 | 292.428 | 7.8015 | 2.2814 | 2281.37
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 811.147 | 49.3823 | 293.805 | 7.1442 | 2.099 | 2099
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 690.287 | 44.3081 | 300.489 | 6.0937 | 1.8311 | 1831.09
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.956 | 40.5384 | 304.939 | 4.8848 | 1.4896 | 1489.57
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 393.798 | 35.6624 | 309.476 | 3.3905 | 1.0493 | 1049.27
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 124.541 | 25.585 | 311.006 | 1.0095 | 0.31397 | 313.968
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.4033 | 22.9774 | 302.565 | 0.39877 | 0.12065 | 120.654
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.8133 | 20.3673 | 299.599 | 0.24337 | 0.072915 | 72.9147
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.9699 | 18.4504 | 288.202 | 0 | 0.02545 | 25.4504
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is not an output in SAM, here is calculated based on SAM’s array voltage and power.

## V1 module db shadows
June 7 2023 |  | Measured |  |  |  |  | SAM
|  | W/m2 | deg C | V | A | W | W/m2 | W/m2 | deg C | Varray | A | kW | W
Hour summer | Hour winter | Measured GPOA | Measured Tmod_ref | Measured Vpv_nss | Measured Ipv_nss | Measured Ppv_nss | SAM GPOA | SAM GPOA with shadows | SAM Tarray | SAM Varray | SAM Iarray | SAM Parray | SAM Parray
0 | 23 | 0 | 7.4742 | 0.15641 | 0.00075203 | 0.00011763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Tilt | 15.6
1 | 0 | 0 | 6.5978 | 0.14946 | 0.00074905 | 0.00011195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Azimuth | 106 | -74
2 | 1 | 0 | 7.5524 | 0.39312 | 0.00074721 | 0.00029374 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 7.4333 | 36.3975 | 0.00061019 | 0.022209 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1.2388 | 6.9078 | 251.539 | 0.0011675 | 0.29368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 27.4707 | 8.0894 | 265.024 | 0.21624 | 57.3086 | 55.438 | 37.4909 | 14.0287 | 306.143 | 0.20871 | 0.063894 | 63.8937
6 | 5 | 244.7736 | 15.3344 | 275.1885 | 0.50031 | 137.6785 | 261.742 | 150.727 | 19.8956 | 320.798 | 1.2924 | 0.41461 | 414.605
7 | 6 | 463.2416 | 29.06 | 246.9347 | 3.6231 | 894.6614 | 442.117 | 435.942 | 30.5216 | 314.869 | 4.0056 | 1.2612 | 1261.24
8 | 7 | 628.2192 | 37.8644 | 241.6963 | 5.7006 | 1377.8053 | 613.687 | 606.998 | 38.5819 | 304.4 | 5.5763 | 1.6974 | 1697.42
9 | 8 | 738.3936 | 44.2469 | 234.634 | 6.8923 | 1617.1691 | 755.715 | 748.429 | 45.9986 | 293.998 | 6.8123 | 2.0028 | 2002.8
10 | 9 | 816.324 | 47.5544 | 231.005 | 7.6777 | 1773.5795 | 857.171 | 849.857 | 49.1072 | 289.301 | 7.6723 | 2.2196 | 2219.61
11 | 10 | 855.0859 | 51.3678 | 226.9802 | 8.0011 | 1816.0959 | 916.099 | 908.723 | 53.0563 | 283.664 | 8.1539 | 2.313 | 2312.97
12 | 11 | 855.8713 | 50.9861 | 227.2452 | 7.9697 | 1811.0721 | 931.451 | 923.891 | 51.388 | 285.789 | 8.2624 | 2.3613 | 2361.3
13 | 12 | 800.7496 | 51.0481 | 227.8847 | 7.4681 | 1701.8622 | 897.3 | 886.436 | 52.2361 | 284.945 | 7.9181 | 2.2562 | 2256.23
14 | 13 | 703.3958 | 48.5761 | 231.5039 | 6.5913 | 1525.9102 | 817.736 | 811.147 | 51.1561 | 286.837 | 7.2528 | 2.0804 | 2080.36
15 | 14 | 583.2092 | 42.665 | 238.706 | 5.3758 | 1283.2424 | 696.89 | 690.287 | 45.8153 | 294.476 | 6.1899 | 1.8228 | 1822.79
16 | 15 | 446.6485 | 36.8389 | 243.4784 | 4.0086 | 976.0168 | 557.139 | 550.956 | 41.7765 | 299.955 | 4.9638 | 1.4889 | 1488.93
17 | 16 | 296.5058 | 30.8408 | 260.6416 | 1.6677 | 434.6752 | 398.921 | 393.798 | 36.563 | 305.781 | 3.4465 | 1.0539 | 1053.88
18 | 17 | 73.4169 | 20.7422 | 248.1827 | 0.48615 | 120.6544 | 242.735 | 124.541 | 25.8446 | 309.527 | 1.0263 | 0.31767 | 317.671
19 | 18 | 40.9356 | 17.8711 | 241.5472 | 0.3889 | 93.9386 | 102.21 | 45.4033 | 23.0865 | 301.541 | 0.40526 | 0.1222 | 122.201
20 | 19 | 23.9405 | 16.0125 | 239.5772 | 0.25496 | 61.0829 | 29.678 | 27.8133 | 20.4336 | 298.709 | 0.2473 | 0.073869 | 73.8694
21 | 20 | 3.5403 | 13.2006 | 236.1876 | 0.076344 | 18.0316 | 12.7767 | 11.9699 | 18.4796 | 287.345 | 0 | 0.02577 | 25.7695
22 | 21 | 0 | 10.8411 | 118.9726 | 0.00054112 | 0.064379 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 22 | 0 | 9.6378 | 1.5047 | 0.00075492 | 0.0011359 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Data is in winter time, graphs are on summer time