## Foglio1
Collector Aperture Area (m2) | 166 |  |  | Inputs
Collector Length (m) | 38 |  |  | Values non consistent
DNI (W/m2) | 850 |  |  | SAM Values
Number of collectors in loop | 16
General optical derate | 0.6
HTF temperature adj Polynomial fit heat loss model (W/m) | 400
Collector Width (m) | 4.3684
Single Loop Length (m) | 608
Single Loop Aperture (m2) | 2656
Solar Power per loop (kW) | 2257.6
Concentrated power per loop (kW) | 1354.56
Total Optical Losses per loop (kW) | 903.04
Total Thermal Losses per loop (kW) | 243.2
Total optica-thermal losses (kW) | 1146.24
Total power to HTF per loop (MW) | 1.1114 | 1.2078 | SAM Value (Solar Field-> Design Point) |  | 1
Loop Thermal Efficiency | 0.82046 | 0.892 | SAM Value (Solar Field-> Design Point)
Total Loop Conversion Efficiency | 0.49227 | 0.535 | SAM Value (Solar Field-> Design Point)