## SAM Exchange
This Spreadsheet provides more detailed cost categories for a Parabolic Trough power plant. For more information see NREL Technical Report NREL/TP-550-47605, July 2010.
General Guidelines and Notes: | Numbers in blue text or blue cells are user inputs
Users can utilize NREL's reference plant to estimate costs for different project plants, or
Users can create their own reference plant and utilize it as the basis for calculating costs for other size plants.
This spreadsheet can be linked to SAM 2009 to exchange values between SAM and the cost model for analyses. Cells where data are exchanged with SAM must have no formatting in Excel.
This tool is meant to supply a template for more detailed cost analysis of Parabolic Trough plants. Supplied values are intended to be representative. Users are encouraged to make changes where they see fit.
[5 empty] | Project Plant Data. Either input by hand or from SAM via Excel Exchange. | Input Value | Units | Variable Name in Spreadsheet | Comments
[5 empty] | Design Gross Output | 110 | MWe | Proj_Turb_Gross
[5 empty] | Actual Aperture | 854000 | m2 | Proj_SF_Area
[5 empty] | TES thermal capacity | 1750 | MWh-t | Proj_TES_Capacity
[5 empty] | User Variable 1 | 2009 |  | Cost_Yr | Analysis year
[5 empty] | Inflation Rate | 2% |  | inflation
[5 empty] | Row spacing | 15 | m | Proj_SCA_Spacing | used to estimate land area
[5 empty] | Aperture width, total structure | 5 | m | Proj_SCA_Aperture | used to estimate land area
[5 empty] | Sales Tax | 7.75% |  | Sales_Tax_Rate
[5 empty] | User Variable 4 | 1 |  | Labor_cost_factor | Scale labor rates for location
[5 empty] | User Variable 5 | 1 |  | PB_cost_multiplier | Used to increase PB cost for air-cooled condenser
Direct Capital Cost Summary | Reference Plant | Totals |  | Units | Project Plant Totals | Totals | SAM Parameter (output to SAM) | Units | SAM Parameter name
Site Improvements |  | 23495000 | 27.5117 | /m2 |  | 23495000 | 28 | $/m2 | Direct Cost - Site Improvements
Solar Field |  | 251758000 | 294.7986 | /m2 |  | 251758000 | 295 | $/m2 | Direct Cost - Solar Field
HTF System |  | 77214000 | 90.4145 | /m2 |  | 77214000 | 90 | $/m2 | Direct Cost - HTF System
Thermal Energy Storage |  | 142470000 | 81.4114 | /kWh-t |  | 142470000 | 81 | $/kWh-t | Direct Cost - Storage
Fossil Backup |  | 0 | 0 | /kWe |  | 0 | 0 | $/kWe | Direct Cost - Fossil Backup
Power Plant |  | 104045000 | 945.8636 | /kWe |  | 104045000 | 946 | $/kWe | Direct Cost - Power Plant (based on Turbine gross)
Contingency |  | 59898000 | 10% |  |  | 59898200 | 10 | % | Contingency (% of Direct Costs)
Total Direct Costs | 658880000 |  |  |  | 658880200
Indirect Capital Cost Summary
EPC Costs |  | 97514000 | 14.8% | of DC |  | 97514266.64 | 14.8 | % of DC | Indirect Cost - EPC
Project, Land, Misc. |  | 25874000 | 3.927% | of DC |  | 25873704.1968 | 3.9 | % of DC | Indirect Cost - Project, Land, Misc
DC's Sales Tax |  | 42639000 | 6.471% | of DC |  | 42638554.75 | 84 | applied to % of DC | Indirect Cost - Sales Tax applies to % of DC
Total Installed Cost | 824907000 |  |  |  | 824906725.5868
O&M Summary
Fixed Annual Cost |  |  | 0 |  |  |  | 0 |  | O&M Fixed Annual Cost
Fixed Cost by Capacity |  |  | 69.0883 | /kW-yr |  |  | 69 | $/kW-yr | O&M Fixed Cost by Capacity
Variable Cost by Generation |  |  | 2.5155 | /MWh |  |  | 908090 | $ | O&M Annual Variable Cost
Fossil Fuel Cost |  |  | 6 | /MMBTU |  |  | 6 | $/MMBTU | O&M Fossil Fuel Cost
Estimated O&M labor force |  |  | 47 |  |  |  | 47 |  | Estimated O&M labor force
Note on I25: Craig Turchi: SAM exchange cells must have no $ or % formatting.
Note on E31: Craig Turchi: This value is based on gross turbine output.

## Cap$
NREL Reference Plant Characteristics - southwest Arizona | [12 empty] | Labor Cost Factor: | 1 | in use
|  |  | Variable Name | [10 empty] | 1.2586 | US national average for Natural resources construction & maintenance
Gross Turbine Capacity | 110 | MWe | Ref_Turb_Gross | [10 empty] | 1 | Phoenix, AZ
Solar Field Aperture Area | 854000 | m2 | Ref_SF_area | [10 empty] | 1.89 | LA/Riverside, CA
Thermal storage capacity | 1750 | MWh-t | Ref_TES_capacity
Annual Net Energy Generation | 361000 | MWh | Ref_Enet_yr
|  | NREL Reference Plant Data |  |  |  |  | Project Plant Data
ITEM | Reference Year | Size (Basis) | Material Cost | Labor Cost | TOTAL | Size Scaling Exponent | Size (Basis) | Matl cost esc. Factor | Matl cost esc. Rate | Matl cost factor | Material Cost | Labor cost esc. Factor | Labor cost esc. rate | Labor Cost | TOTAL | Category Contingency
DIRECT CAPITAL COSTS
Site - Site Preparation | 2009 | 854000 | 1342000 | 457000 | 1799000 | 0.9 | 854000 | 10 | 1 | 1 | 1342000 | 11 | 1 | 457000 | 1799000
Site - Clearing & Grubbing | 2009 | 854000 | 0 | 376000 | 376000 | 0.9 | 854000 | 10 | 1 | 1 | 0 | 11 | 1 | 376000 | 376000
Site - Grading, Drainage, Remediation, Retention, & Detention | 2009 | 854000 | 6850000 | 2892000 | 9742000 | 0.9 | 854000 | 10 | 1 | 1 | 6850000 | 11 | 1 | 2892000 | 9742000
Site - Roads, Parking, Fencing | 2009 | 854000 | 9026000 | 1150000 | 10176000 | 0.9 | 854000 | 10 | 1 | 1 | 9026000 | 11 | 1 | 1150000 | 10176000
Site - Water Supply Infrastructure | 2009 | 854000 | 1107000 | 295000 | 1402000 | 0.9 | 854000 | 6 | 1 | 1 | 1107000 | 11 | 1 | 295000 | 1402000
|  |  | 18325000 | 5170000 | 23495000 | [5 empty] | 18325000 |  |  | 5170000 | 23495000 | 10%
Solar Field - Solar Collector Mirrors | 2009 | 854000 | 40635000 | 0 | 40635000 | 1 | 854000 | 14 | 1 | 1 | 40635000 | 11 | 1 | 0 | 40635000
Solar Field - Solar Collector Receiver Tubes & Fittings | 2009 | 854000 | 59429000 | 0 | 59429000 | 1 | 854000 | 6 | 1 | 1 | 59429000 | 11 | 1 | 0 | 59429000
Solar Field - Solar Collector Frame | 2009 | 854000 | 67702000 | 0 | 67702000 | 1 | 854000 | 10 | 1 | 1 | 67702000 | 11 | 1 | 0 | 67702000
Solar Field - Solar Collector Assembly Misc. Components | 2009 | 854000 | 1708000 | 0 | 1708000 | 1 | 854000 | 6 | 1 | 1 | 1708000 | 11 | 1 | 0 | 1708000
Solar Field - Foundations & Support Structures | 2009 | 854000 | 15310000 | 0 | 15310000 | 1 | 854000 | 10 | 1 | 1 | 15310000 | 11 | 1 | 0 | 15310000
Solar Field - Instrument & Controls | 2009 | 854000 | 6792000 | 44000 | 6836000 | 1 | 854000 | 9 | 1 | 1 | 6792000 | 11 | 1 | 44000 | 6836000
Solar Field - Electrical | 2009 | 854000 | 1831000 | 848000 | 2679000 | 1 | 854000 | 9 | 1 | 1 | 1831000 | 11 | 1 | 848000 | 2679000
Solar Field - Labor Installation | 2009 | 854000 | 0 | 53211000 | 53211000 | 1 | 854000 | 30 | 1 | 1 | 0 | 11 | 1 | 53211000 | 53211000
Solar Field - Fabrication tent | 2009 | 854000 | 830000 | 227000 | 1057000 | 1 | 854000 | 12 | 1 | 1 | 830000 | 11 | 1 | 227000 | 1057000
Solar Field - Empirical Sun Tracker | 2009 | 854000 | 3191000 | 0 | 3191000 | 1 | 854000 | 7 | 1 | 1 | 3191000 | 11 | 1 | 0 | 3191000
|  |  | 197428000 | 54330000 | 251758000 | [5 empty] | 197428000 |  |  | 54330000 | 251758000 | 10%
HTF - Freeze Protection System | 2009 | 854000 | 436000 | 33000 | 469000 | 0.9 | 854000 | 4 | 1 | 1 | 436000 | 11 | 1 | 33000 | 469000
HTF - Ullage System | 2009 | 854000 | 810000 | 116000 | 926000 | 0.9 | 854000 | 4 | 1 | 1 | 810000 | 11 | 1 | 116000 | 926000
HTF - Pumps | 2009 | 854000 | 4856000 | 210000 | 5066000 | 0.9 | 854000 | 8 | 1 | 1 | 4856000 | 11 | 1 | 210000 | 5066000
HTF - Expansion & Nitrogen Blanketing Systems | 2009 | 854000 | 5636000 | 901000 | 6537000 | 0.9 | 854000 | 4 | 1 | 1 | 5636000 | 11 | 1 | 901000 | 6537000
HTF - Solar Field Piping, Insulation, Valves, & Fittings | 2009 | 854000 | 29410000 | 12790000 | 42200000 | 1 | 854000 | 6 | 1 | 1 | 29410000 | 11 | 1 | 12790000 | 42200000
HTF - Power Block Piping, Insulation, Valves, & Fittings | 2009 | 854000 | 913000 | 87000 | 1000000 | 0.9 | 854000 | 6 | 1 | 1 | 913000 | 11 | 1 | 87000 | 1000000
HTF - Foundations & Support Structures | 2009 | 854000 | 1227000 | 615000 | 1842000 | 0.9 | 854000 | 10 | 1 | 1 | 1227000 | 11 | 1 | 615000 | 1842000
HTF - Fluid | 2009 | 854000 | 19174000 | 0 | 19174000 | 1 | 854000 | 16 | 1 | 1 | 19174000 | 11 | 1 | 0 | 19174000
|  |  | 62462000 | 14752000 | 77214000 | [5 empty] | 62462000 |  |  | 14752000 | 77214000 | 10%
TES - Pumps & Heat Exchangers | 2009 | 1750 | 27794000 | 1972000 | 29766000 | 0.8 | 1750 | 3 | 1 | 1 | 27794000 | 11 | 1 | 1972000 | 29766000
TES - Tanks | 2009 | 1750 | 37412000 | 5470000 | 42882000 | 0.8 | 1750 | 4 | 1 | 1 | 37412000 | 11 | 1 | 5470000 | 42882000
TES - Storage Fluid | 2009 | 1750 | 61300000 | 907000 | 62207000 | 1 | 1750 | 21 | 1 | 1 | 61300000 | 11 | 1 | 907000 | 62207000
TES - Piping, Insulation, Valves, & Fittings | 2009 | 1750 | 1030000 | 388000 | 1418000 | 0.8 | 1750 | 6 | 1 | 1 | 1030000 | 11 | 1 | 388000 | 1418000
TES - Foundations & Support Structures | 2009 | 1750 | 290000 | 230000 | 520000 | 0.8 | 1750 | 10 | 1 | 1 | 290000 | 11 | 1 | 230000 | 520000
TES - Instrumentation & Controls | 2009 | 1750 | 2659000 | 3018000 | 5677000 | 0.8 | 1750 | 7 | 1 | 1 | 2659000 | 11 | 1 | 3018000 | 5677000
|  |  | 130485000 | 11985000 | 142470000 | [5 empty] | 130485000 |  |  | 11985000 | 142470000 | 10%
Fossil Backup | 2009 | 110 | 0 | 0 | 0 | 0.8 | 110 | 3 | 1 | 1 | 0 | 11 | 1 | 0 | 0 | 10%
Power Plant - Steam Turbine Generator Island | 2009 | 110 | 32450000 | 1464000 | 33914000 | 0.8 | 110 | 5 | 1 | 1 | 32450000 | 11 | 1 | 1464000 | 33914000
Power Plant - Solar Steam Generator Equipment | 2009 | 110 | 5714000 | 232000 | 5946000 | 0.8 | 110 | 4 | 1 | 1 | 5714000 | 11 | 1 | 232000 | 5946000
Power Plant - Blowdown System | 2009 | 110 | 162000 | 34000 | 196000 | 0.8 | 110 | 8 | 1 | 1 | 162000 | 11 | 1 | 34000 | 196000
Power Plant - Cooling Systems | 2009 | 110 | 5020000 | 160000 | 5180000 | 0.8 | 110 | 3 | 1 | 1 | 5020000 | 11 | 1 | 160000 | 5180000
Power Plant - Condensate System | 2009 | 110 | 672000 | 183000 | 855000 | 0.8 | 110 | 6 | 1 | 1 | 672000 | 11 | 1 | 183000 | 855000
Power Plant - Feedwater System | 2009 | 110 | 4395000 | 614000 | 5009000 | 0.8 | 110 | 8 | 1 | 1 | 4395000 | 11 | 1 | 614000 | 5009000
Power Plant - Auxiliary Cooling Water System | 2009 | 110 | 814000 | 348000 | 1162000 | 0.8 | 110 | 6 | 1 | 1 | 814000 | 11 | 1 | 348000 | 1162000
Power Plant - Steam Piping, Insulation, Valves, & Fittings | 2009 | 110 | 3903000 | 929000 | 4832000 | 0.8 | 110 | 6 | 1 | 1 | 3903000 | 11 | 1 | 929000 | 4832000
Power Plant - Fuel Gas Handling & Metering System | 2009 | 110 | 193000 | 239000 | 432000 | 0.8 | 110 | 6 | 1 | 1 | 193000 | 11 | 1 | 239000 | 432000
Power Plant - Water Treatment System | 2009 | 110 | 1584000 | 444000 | 2028000 | 0.8 | 110 | 3 | 1 | 1 | 1584000 | 11 | 1 | 444000 | 2028000
Power Plant - Power Distribution Systems | 2009 | 110 | 15737000 | 421000 | 16158000 | 0.8 | 110 | 9 | 1 | 1 | 15737000 | 11 | 1 | 421000 | 16158000
Power Plant - Back-up Power Systems | 2009 | 110 | 479000 | 7000 | 486000 | 0.8 | 110 | 9 | 1 | 1 | 479000 | 11 | 1 | 7000 | 486000
Power Plant - Instrumentation & Controls System | 2009 | 110 | 2804000 | 540000 | 3344000 | 0.8 | 110 | 7 | 1 | 1 | 2804000 | 11 | 1 | 540000 | 3344000
Power Plant - Fire Protection System | 2009 | 110 | 3596000 | 310000 | 3906000 | 0.8 | 110 | 4 | 1 | 1 | 3596000 | 11 | 1 | 310000 | 3906000
Power Plant - Foundations & Support Structures | 2009 | 110 | 3550000 | 2795000 | 6345000 | 0.8 | 110 | 10 | 1 | 1 | 3550000 | 11 | 1 | 2795000 | 6345000
Power Plant - Buildings | 2009 | 110 | 3169000 | 11000 | 3180000 | 0.8 | 110 | 12 | 1 | 1 | 3169000 | 11 | 1 | 11000 | 3180000
Power Plant - BOP Mechanical Systems | 2009 | 110 | 4210000 | 999000 | 5209000 | 0.8 | 110 | 4 | 1 | 1 | 4210000 | 11 | 1 | 999000 | 5209000
Power Plant - BOP Electrical Systems | 2009 | 110 | 3007000 | 2856000 | 5863000 | 0.8 | 110 | 9 | 1 | 1 | 3007000 | 11 | 1 | 2856000 | 5863000
|  |  | 91459000 | 12586000 | 104045000 | [5 empty] | 91459000 |  |  | 12586000 | 104045000 | 10%
Direct Capital Cost Subtotal |  |  | 500159000 | 98823000 | 598982000 |  | Direct Capital Cost Subtotal |  |  |  | 500159000 |  |  | 98823000 | 598982000
Contingency (total) |  |  |  |  | 59898000 |  | Contingency (total) | [7 empty] | 59898200
Contingency (% of Direct Capital Costs) |  |  |  | 10% |  |  | Contingency (% of Direct Capital Costs) | [7 empty] | 10%
Direct Capital Costs Total |  |  |  |  | 658880000 |  | Direct Capital Costs Total | [7 empty] | 658880200
INDIRECT PROJECT COSTS |  | Size (Basis) | % of Basis | Fixed Value |  |  | INDIRECT PROJECT COSTS
ENGINEER, PROCURE, CONSTRUCT COSTS: | [6 empty] | Size (Basis)
Engineering (EPCM basis) | 2009 | 658880000 | 2% | 0 | 13177600 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 13177603.6
Construction management (EPCM basis) | 2009 | 658880000 | 1.6% | 0 | 10542080 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 10542082.88
Commissioning / start-up (EPCM basis) | 2009 | 658880000 | 0.2% | 0 | 1317760 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 1317760.36
Owner's Engg & Project Mgmt | 2009 | 658880000 | 7% | 0 | 46121600 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 46121612.6
Interest during Construction | 2009 | 658880000 | 4% | 0 | 26355200 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 26355207.2
EPC Costs Subtotal |  |  |  |  | 97514240 |  | EPC Costs Subtotal | [7 empty] | 97514266.64
PROJECT, LAND, MISC COSTS:
Permitting, Licensing, Legal | 2009 | 658880000 | 1% | 10000000 | 16588800 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 16588801.8
Land (acres) | 2009 | 928.4902 | 10000 | per acre | 9284902.3968 |  | 928.4902 |  |  |  | 10000 | per acre |  |  | 9284902.3968
Other | 2009 | 658880000 | 0% | 0 | 0 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 0
Other | 2009 | 658880000 |  |  | 0 | 0.9 | 658880200 |  |  |  |  | 13 | 1 |  | 0
OTHER COSTS: | [6 empty] | OTHER COSTS:
Builder's All Risk Insurance |  |  |  |  | #REF! |  | Builder's All Risk Insurance | [7 empty] | #REF!
Worker's Compensation & Employers' Liability |  |  |  |  | #REF! |  | Worker's Compensation & Employers' Liability | [7 empty] | #REF!
Commercial General Liability |  |  |  |  | #REF! |  | Commercial General Liability | [7 empty] | #REF!
Payment & Performance Bond |  |  |  |  | #REF! |  | Payment & Performance Bond | [7 empty] | #REF!
Owner's Cost |  |  |  |  | #REF! |  | Owner's Cost | [7 empty] | #REF!
Indir Startup Spares |  |  |  |  | #REF! |  | Indir Startup Spares | [7 empty] | #REF!
Contractor's Engineering |  |  |  |  | #REF! |  | Contractor's Engineering | [7 empty] | #REF!
Escalation |  |  |  |  | #REF! |  | Escalation | [7 empty] | #REF!
Project, Land, Misc. |  |  |  |  | #REF! |  | Project, Land, Misc. | [7 empty] | #REF!
%DC's Sales Tax Applies |  |  |  |  | #REF! |  | %DC's Sales Tax Applies | [7 empty] | #REF!
Legal Expenses |  |  |  |  | #REF! |  | Legal Expenses | [7 empty] | #REF!
Warranty |  |  |  |  | #REF! |  | Warranty | [7 empty] | #REF!
Permits & Fees |  |  |  |  | #REF! |  | Permits & Fees | [7 empty] | #REF!
Other Costs Subtotal |  |  |  |  | #REF! |  | Other Costs Subtotal | [7 empty] | #REF!
Project, Land, Misc Costs Subtotal |  |  |  |  | 25873702.3968 |  | Project, Land, Misc Costs Subtotal | [7 empty] | 25873704.1968
SALES TAX | [6 empty] | SALES TAX
Tax Rate (input from SAM) | 7.75% | [5 empty] | Tax Rate (input on SAM Exchange sheet) |  |  |  |  | 7.75%
Tax Basis (Direct Capital Material Costs incl Contingency) |  | 550174900 |  |  |  |  | Tax Basis (Direct Capital Material Costs incl Contingency) | [6 empty] | 550174900
Basis percentage of Total Direct Costs incl Contingency |  |  | 83.5% |  |  |  | Basis percentage of Total Direct Costs incl Contingency | [6 empty] | 83.5%
Sales Tax Cost Subtotal |  |  |  |  | 42638554.75 |  | Sales Tax Cost Subtotal | [7 empty] | 42638554.75
Note on F9: Craig Turchi: Reference Plant is based on Arizona wage rates.
Note on I9: Craig Turchi: Project Plant costs are calculated by: (Ref Plant Cost) * (Proj Plant Size / Ref Plant Size)^(scaling exponent)
Note on K9: Craig Turchi: Enter number corresponding to the desired Cost index Factor Num. on sheet CI
Note on M9: Craig Turchi: Cost factors allow the user to adjust material costs without changing the spreadsheet formula, for example to simulate a new technology
Note on O9: Craig Turchi: Enter number corresponding to the desired Cost index Factor Num. on sheet CI
Note on E42: Craig Turchi: Assumes salt at $1.00/kg.

## O&M$
Reference Plant Characteristics - see Cap$ sheet |  |  | Variable Name | [7 empty] | Labor Cost Factor: | see Cap$ cell Q1
Labor Burden Rate | 50% |  | DL_burden
| Reference Plant Data | [6 empty] | Project Plant Data
ITEM | Reference Year | Size (Basis) | Qty | Annual Salary Arizona Location ($/yr) | Burdened Labor Cost |  | Size Scaling Exponent | Size | Labor cost esc. Factor | Labor cost esc. rate | Cost factor | Burdened Labor Cost | Workers
Admininstration Labor
Admin - Plant Manager | 2008 | 854000 | 1 | 95000 | 142500 |  | 0 | 854000 | 13 | 0.98286 | 1 | 140057.0275 | 1
Admin - Administrative Aide | 2008 | 854000 | 1 | 33000 | 49500 |  | 0 | 854000 | 11 | 1.0178 | 1 | 50380.9061 | 1
Admin - Financial Manager | 2008 | 854000 | 1 | 87000 | 130500 |  | 0 | 854000 | 13 | 0.98286 | 1 | 128262.7515 | 1
Admin - Purchasing | 2008 | 854000 | 1 | 51000 | 76500 |  | 0 | 854000 | 13 | 0.98286 | 1 | 75188.5095 | 1
Admin - Human Resources | 2008 | 854000 | 1 | 56000 | 84000 |  | 0 | 854000 | 13 | 0.98286 | 1 | 82559.932 | 1
Admin - Plant Engineer | 2008 | 854000 | 1 | 92000 | 138000 |  | 0 | 854000 | 13 | 0.98286 | 1 | 135634.174 | 1
Admin - Performance Engineer | 2008 | 854000 | 1 | 63000 | 94500 |  | 0 | 854000 | 13 | 0.98286 | 1 | 92879.9235 | 1
Admin - Information Technology | 2008 | 854000 | 1 | 87000 | 130500 |  | 0 | 854000 | 13 | 0.98286 | 1 | 128262.7515 | 1
Admin - Clerk | 2008 | 854000 | 0 | 32000 | 0 |  | 0 | 854000 | 13 | 0.98286 | 1 | 0 | 0
Admin - | 2008 | 854000 | 0 | 0 | 0 |  | 0 | 854000 | 13 | 0.98286 | 1 | 0 | 0
|  |  | 8 |  | 846000 | [6 empty] | 833225.9755 | 8
Operations Labor
Ops - Operations Manager | 2008 | 854000 | 1 | 84000 | 126000 |  | 0 | 854000 | 13 | 0.98286 | 1 | 123839.898 | 1
Ops - Asst Ops Manager | 2008 | 854000 | 0 | 63000 | 0 |  | 0 | 854000 | 13 | 0.98286 | 1 | 0 | 0
Ops - Senior Operators | 2008 | 854000 | 1 | 44000 | 66000 |  | 0 | 854000 | 11 | 1.0178 | 1 | 67174.5415 | 1
Ops - Control Room Operator | 2008 | 854000 | 4 | 40000 | 240000 |  | 0 | 854000 | 11 | 1.0178 | 1 | 244271.06 | 4
Ops - Plant Equipment Operator | 2008 | 854000 | 6 | 40000 | 360000 |  | 1 | 854000 | 11 | 1.0178 | 1 | 366406.59 | 6
Ops - Asst Plant Equipment Operator | 2008 | 854000 | 1 | 36000 | 54000 |  | 1 | 854000 | 11 | 1.0178 | 1 | 54960.9885 | 1
Ops - Technician | 2008 | 854000 | 2 | 40000 | 120000 |  | 1 | 854000 | 11 | 1.0178 | 1 | 122135.53 | 2
Ops - | 2008 | 854000 | 0 | 0 | 0 |  | 1 | 854000 | 11 | 1.0178 | 1 | 0 | 0
Ops - | 2008 | 854000 | 0 | 0 | 0 |  | 1 | 854000 | 11 | 1.0178 | 1 | 0 | 0
|  |  | 15 |  | 966000 | [6 empty] | 978788.608 | 15
Power Block / TES Maintenance Labor
PB - Maintenance Supervisor | 2008 | 110 | 1 | 48000 | 72000 |  | 0 | 110 | 13 | 0.98286 | 1 | 70765.656 | 1
PB - Maintenance Foreman | 2008 | 110 | 1 | 44000 | 66000 |  | 0 | 110 | 13 | 0.98286 | 1 | 64868.518 | 1
PB - Electrician | 2008 | 110 | 1 | 44000 | 66000 |  | 0.7 | 110 | 11 | 1.0178 | 1 | 67174.5415 | 1
PB - Instrument Technician | 2008 | 110 | 2 | 40000 | 120000 |  | 0.7 | 110 | 11 | 1.0178 | 1 | 122135.53 | 2
PB - Machinist/Welder/Mechanical Technician | 2008 | 110 | 4 | 40000 | 240000 |  | 0.7 | 110 | 11 | 1.0178 | 1 | 244271.06 | 4
PB - Clerk/Assistant | 2008 | 110 | 1 | 32000 | 48000 |  | 0.7 | 110 | 11 | 1.0178 | 1 | 48854.212 | 1
PB - | 2008 | 110 | 0 | 0 | 0 |  | 0.7 | 110 | 11 | 1.0178 | 1 | 0 | 0
PB - | 2008 | 110 | 0 | 0 | 0 |  | 0.7 | 110 | 11 | 1.0178 | 1 | 0 | 0
|  |  | 10 |  | 612000 | [6 empty] | 618069.5175 | 10
Solar Field Maintenance Labor
SF - Maintenance Supervisor | 2008 | 854000 | 1 | 48000 | 72000 |  | 0 | 854000 | 13 | 0.98286 | 1 | 70765.656 | 1
SF - Maintenance Foreman | 2008 | 854000 | 1 | 44000 | 66000 |  | 0 | 854000 | 13 | 0.98286 | 1 | 64868.518 | 1
SF - Instrument Technician | 2008 | 854000 | 2 | 40000 | 120000 |  | 1 | 854000 | 11 | 1.0178 | 1 | 122135.53 | 2
SF - Machinist/Welder/Mechanical Technician | 2008 | 854000 | 6 | 40000 | 360000 |  | 1 | 854000 | 11 | 1.0178 | 1 | 366406.59 | 6
SF - Clerk/Assistant | 2008 | 854000 | 4 | 32000 | 192000 |  | 1 | 854000 | 11 | 1.0178 | 1 | 195416.848 | 4
SF - | 2008 | 854000 | 0 | 0 | 0 |  | 1 | 854000 | 11 | 1.0178 | 1 | 0 | 0
SF - | 2008 | 854000 | 0 | 0 | 0 |  | 1 | 854000 | 11 | 1.0178 | 1 | 0 | 0
|  |  | 14 |  | 810000 | [6 empty] | 819593.142 | 14
Labor Subtotal |  |  | 47 |  | 3234000 | [6 empty] | 3249677.243 | 47
| Reference Year | Size (Basis) | Units/yr | Rate ($/unit) | Cost |  |  | Size | Cost esc. Factor | Cost esc. rate | Cost factor | Cost
Service Contracts
SCon - Control Systems | 2009 | 1 | 1 | 100000 | 100000 |  | 1 | 1 | 11 | 1 | 1 | 100000
SCon - Computers/Office Equipment | 2009 | 47 | 1 | 105000 | 105000 |  | 1 | 47 | 11 | 1 | 1 | 105000
SCon - Grounds/house keeping | 2009 | 854000 | 1 | 100000 | 100000 |  | 0.5 | 854000 | 11 | 1 | 1 | 100000
SCon - Mirror washing | 2009 | 854000 | 1 | 350000 | 350000 |  | 1 | 854000 | 30 | 1 | 1 | 350000
SCon - Water Treatment | 2009 | 110 | 1 | 145000 | 145000 |  | 1 | 110 | 30 | 1 | 1 | 145000
SCon - | 2009 | 1 | 0 |  | 0 |  | 1 | 1 | 30 | 1 | 1 | 0
[5 empty] | 800000 | [6 empty] | 800000
Utilities
Util - Natural Gas (MMBTU) | 2009 | 110 | 8900 | 6 | 53400 |  | 1 | 110 | 30 | 1 | 1 | 53400
Util - Water (acre/ft) | 2009 | 110 | 1241 | 450 | 558450 |  | 1 | 110 | 30 | 1 | 1 | 558450
Util - Auxiliary Power (MWh) | 2009 | 110 | 3703 | 80 | 296240 |  | 1 | 110 | 30 | 1 | 1 | 296240
[5 empty] | 908090 | [6 empty] | 908090
| Reference Year | Size (Basis) | Fraction of Cost basis | Ref Plant Cost Basis | Cost |  |  | Size | Cost esc. Factor | Cost esc. rate | Cost factor | Cost
Materials & Maintenance (% of Capital Cost Basis)
Misc - Site | 2009 | 854000 | 0.003 | 23495000 | 70485 |  | 1 | 854000 | 30 | 1 | 1 | 70485
Misc - Solar Field | 2009 | 854000 | 0.003 | 251758000 | 755274 |  | 1 | 854000 | 30 | 1 | 1 | 755274
Misc - HTF | 2009 | 854000 | 0.003 | 77214000 | 231642 |  | 1 | 854000 | 30 | 1 | 1 | 231642
Misc - TES | 2009 | 1750 | 0.003 | 142470000 | 427410 |  | 0.7 | 1750 | 30 | 1 | 1 | 427410
Misc - Fossil Backup | 2009 | 110 | 0.01 | 0 | 0 |  | 0.7 | 110 | 30 | 1 | 1 | 0
Misc - Powerblock | 2009 | 110 | 0.02 | 104045000 | 2080900 |  | 0.7 | 110 | 30 | 1 | 1 | 2080900
[5 empty] | 3565711 | [6 empty] | 3565711
Annual O&M Summary (Reference) | [7 empty] | Annual O&M Summary (Project)
Burdened Labor |  |  |  |  | 3234000 | fixed |  | Burdened Labor |  |  |  | 3249677.243
Service Contracts |  |  |  |  | 800000 | fixed |  | Service Contracts |  |  |  | 800000
Utilities |  |  |  |  | 908090 | variable |  | Utilities |  |  |  | 908090
Materials & Misc |  |  |  |  | 3565711 | fixed |  | Materials & Misc |  |  |  | 3565711
[5 empty] | 8507801 | [6 empty] | 8523478.243
|  |  |  | Fixed Cost by Capacity ($/kW-yr) | 69.0883 |  |  |  |  | Fixed Cost by Capacity ($/kW-yr) |  | 69.2308
|  |  |  | Variable Cost by Generation ($/MWh) | 2.5155 |  |  |  |  | Annual Variable Cost ($) |  | 908090
Note on F6: Craig Turchi: Reference salaries based on national means from US Bureau of Labor under NAICS 221100, Electric Power Generation, Transmission and Distribution, May 2008. National means adjusted to Arizona Reference plant location by ratio of (1/1.26).
Note on I6: Craig Turchi: Project Plant costs are calculated by: (Ref Plant Cost) * (Proj Plant Size / Ref Plant Size)^(scaling exponent)
Note on M6: Craig Turchi: Cost factors allow the user to adjust project costs without changing the spreadsheet formula.
Note on M53: Craig Turchi: Cost factors allow the user to adjust project costs without changing the spreadsheet formula.
Note on M68: Craig Turchi: Cost factors allow the user to adjust project costs without changing the spreadsheet formula.

## CI
Cost Index Sheet
Data Source: | [12 empty] | Data Source: | [6 empty] | User Defined
Chemical Engineering Plant Cost Index (CEPCI) | [12 empty] | Producer Price Index (PPI)
http://www.che.com/ | [12 empty] | http://www.bls.gov/ppi/
Factor Num = | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Period | CE INDEX | Equipment | Heat Exchangers and Tanks | Process Machinery | Pipe, valves and fittings | Process Instruments | Pumps and Compressors | Electrical equipment | Structural supports | Construction Labor | Buildings | Engineering Supervision | PPI WPU1311 Flat Glass | PPI WPU06520135 Syn NH3 | PPI WPU06140197 Aromatic Chems |  |  |  |  | Solar Salt ($/MT) | [8 empty] | None
1998 | 389.5 | 436 | 382.8 | 430.8 | 534.8 | 365.3 | 648.5 | 333.6 | 394.3 | 287.4 | 374.2 | 341.2 | 107.1 | [15 empty] | 1
1999 | 390.6 | 435.5 | 371.2 | 433.6 | 531.6 | 363.5 | 658.4 | 335.8 | 413.1 | 292.5 | 380.2 | 339.9 | 106.4 | [15 empty] | 1
2000 | 394.1 | 438 | 370.6 | 439.4 | 545.9 | 368.5 | 665.3 | 339.4 | 408.7 | 299.2 | 385.6 | 340.6 | 109.7 | [15 empty] | 1
2001 | 394.3 | 437.3 | 363.9 | 439.5 | 548.1 | 362.9 | 683.2 | 341.2 | 413.9 | 302.3 | 385.6 | 341.5 | 112 | [6 empty] | 400 | [8 empty] | 1
2002 | 395.6 | 437.5167 | 356.925 | 444.15 | 555.8417 | 363.5083 | 699.1917 | 341.3583 | 415.45 | 305.7917 | 390.4167 | 345.3333 | 111.2417 |  | 100.3 |  |  |  |  | 520 | [8 empty] | 1
2003 | 402.0833 | 445.475 | 363.5333 | 451.5417 | 570.8 | 365.3833 | 705.3083 | 341.5833 | 428.4833 | 308.8167 | 400.1667 | 347.4167 | 110.975 | 101.0429 | 126 |  |  |  |  | 650 | [8 empty] | 1
2004 | 444.225 | 508.125 | 464.825 | 490.9833 | 600.625 | 374.3333 | 719.4333 | 351.0167 | 537.4833 | 307.7333 | 428.5667 | 345.1833 | 108.5833 | 115.05 | 181.4 |  |  |  |  | 780 | [8 empty] | 1
2005 | 468.1667 | 543.675 | 513.9333 | 519.65 | 623.7 | 381.825 | 752.5 | 372.1417 | 584.7667 | 305.55 | 445.1 | 346.7917 | 110.9833 | 132.2167 | 224.2 |  |  |  |  | 900 | [8 empty] | 1
2006 | 499.55 | 588.0417 | 547.95 | 549.7083 | 708.0083 | 420.125 | 785.7333 | 403.0667 | 625.3 | 309.3167 | 468.5667 | 350.925 | 113.4583 | 139.5583 | 272.5 |  |  |  |  | 1020 | [8 empty] | 1
2007 | 525.4167 | 624.3583 | 592.1083 | 598.2667 | 733.6 | 425.25 | 831.175 | 430.4667 | 662.6167 | 315.125 | 476.775 | 357.0083 | 114.1667 | 156 | 287.3 |  |  |  |  | 1150 | [8 empty] | 1
2008 | 575.4 | 696.8 | 687.6 | 643.4 | 827.6 | 434.6 | 871.7 | 458.5 | 748.6 | 321.7 | 506.9 | 352.9 | 114.7 | 240.3 | 323.7 |  |  |  |  | 1300 | [8 empty] | 1
2009 | 521.925 | 615.675 | 558.325 | 598.55 | 760.7333 | 397.4667 | 897.2667 | 461.525 | 629.15 | 327.425 | 492.0333 | 346.85 | 115 | 169 | 251.9 |  |  |  |  | 1080 | [8 empty] | 1
2010 | 550.8083 | 659.3833 | 610.4 | 622.4917 | 824.4167 | 422.1833 | 902.6333 | 478.7167 | 679.9833 | 328.8917 | 504.325 | 339.0583 | 111.2 | 171.4 | 331.3 |  |  |  |  | 1200 | [8 empty] | 1
2011 | 585.9833 | 713.2917 | 675.8667 | 666.6917 | 889.1667 | 437.8083 | 903.6417 | 506.2583 | 754.9917 | 327.3917 | 517.1333 | 332.3667 | 112.8 | 237.1 | 432.3 |  |  |  |  | 1200 | [8 empty] | 1
2012 | 584.6167 | 712.5417 | 661.65 | 668.7333 | 913.7583 | 425.7917 | 920.1333 | 512.4667 | 754.5833 | 322.5917 | 525.6167 | 328.175 | 114.6 | 245.5 | 443 |  |  |  |  | 1200 | [8 empty] | 1
2013 | 566.4 | 685.4 | 624.3 | 655 | 863.4 | 410.8 | 919.3 | 513.1 | 741.7 | 319.1 | 534 | 326 | 118.4 | 293.8 | 435.8 |  |  |  |  | 900 | [8 empty] | 1
2014 | [28 empty] | 1
2015 | [28 empty] | 1
2016 | [28 empty] | 1
2017 | [28 empty] | 1
2018 | [28 empty] | 1
2019 | [28 empty] | 1
2020 | [28 empty] | 1
Note on U6: Craig Turchi: NREL estimate from industry sources in $ per metric tonne.
Note on A22: CST: Provisional values for May 2013