## SAM Exchange
This Spreadsheet provides more detailed cost categories for a Power Tower or Central Receiver power plant. The structure is patterned after the model developed for a Parabolic Trough plant in NREL Technical Report NREL/TP-550-47605, July 2010.
General Guidelines and Notes: | Numbers in blue text or blue cells are user inputs
The Tower Roadmap (SAND2011-2419) assumes contingency with each subsystem. The Reference Case in this spreadsheet and SAM applies a single contingency to all Direct Costs.
| References: | Parabolic Trough Cost Model, NREL/TP-550-47605, July 2010.
Power Tower Technology Roadmap, SAND2011-2419, April 2011.
Kelly, B., "Advanced Thermal Storage for Central Receivers with Supercritical Coolants," Abengoa Solar, final report under DE-FG36-08GO18149, June 15, 2010.
Molten Salt Power Tower Cost for Modeling with the System Advisor Model (SAM), NREL/TP-xxxx-xxxxx, 2013.
| Reference Plant Data sent to SAM |  | Output to SAM |  | Project Plant Data. Either input by hand or from SAM via Excel Exchange. | Input Value | Units | Variable Name in Spreadsheet | Comments
| Fixed Tower Cost Factor at Cost_Yr |  | 3100000 | $ | Design Turbine Gross Output | 115 | MWe | Proj_Turb_Gross
| Receiver Reference Cost at Cost_Yr |  | 104600000 | $ | Design Thermal Power | 279 | MW-t | PB_Thermal_Design_Capacity
| Receiver Reference Area |  | 1571 | m2 | Full Load Hours of TES | 10 | hr | Proj_TES_hrs
| Receiver cost scaling exponent |  | 0.7 |  | Total Land Area | 1953 | acres | Proj_land_area
[5 empty] | Total Reflective Area | 1289000 | m2 | Proj_SF_Area | Solar field aperture area
[5 empty] | Receiver Design Thermal Power | 670 | MW-t | Proj_Rcvr_MWt
[5 empty] | Area | 1133 | m2 | Proj_Rcvr_area | Receiver area
[5 empty] | Tower Height | 203 | m | Proj_Tower_Height
[5 empty] | Inflation Rate | 0.025 |  | inflation
[5 empty] | Sales Tax | 0.05 |  | Sales_Tax_Rate
[5 empty] | User Variable 1 | 2012 |  | Cost_Yr | analysis year
[5 empty] | User Variable 2 | 1 |  | Labor_cost_factor | Scale labor rates for location
Direct Capital Cost Summary | Reference Plant | Totals |  | Units | Project Plant Totals | Totals | SAM Parameter (output to SAM) | Units | SAM Parameter name
Site Improvements |  | 10994540 | 10800.1375 | /acre |  | 21476402.9574 | 17 | $/m2 | Site Improvement Cost per m2
Heliostat Field |  | 233500000 | 181.1482 | /m2 |  | 233500000 | 181 | $/m2 | Heliostat Field Cost per m2
Tower |  | 28500000 |  |  |  | 29791687.3946 |  |  | not sent to SAM
Receiver |  | 97020000 | 106.6154 | /kW-t |  | 85113356.7036 | 127.0349 | /kW-t | not sent to SAM
Thermal Energy Storage |  | 73600000 | 26.3799 | /kWh-t |  | 76248130.1989 | 27 | $/kWh-t | Storage Cost per kWht
Fossil Backup |  | 0 | 0 | /kWe |  | 0 | 0 | $/kWe | Fossil Backip Cost per kWe
Balance of Plant |  | 40770000 | 354.5217 | /kWe |  | 40770000 | 355 | $/kWe | Balance of Plant Cost per kWe
Power Plant |  | 138050000 | 1200.4348 | /kWe |  | 138050000 | 1200 | $/kWe | Power Block Cost per kWe (based on Turbine gross)
Contingency |  | 43570000 | 7% |  |  | 43746470.4078 | 7 | % | Contingency (% of Direct Costs)
Total Direct Costs | 666004540 |  |  |  | 668696047.6623
Indirect Capital Cost Summary
EPC and Owner Costs |  | 73260000 | 11% | of DC |  | 73526904.8964 | 11 | % of DC | EPC Costs % Direct
Land |  | 10180000 | 10000 | /acre |  | 19530000 | 10000 | Land cost per acre | Land Costs acre
DC's Sales Tax |  | 26049000 | 3.911% | of DC |  | 26201303.4001 | 78 | applied to % of DC | Sales Tax Percentage of Direct Costs
Total Installed Cost | 775493540 |  |  |  | 787954255.9588
O&M Summary
Fixed Annual Cost |  |  | 0 |  |  |  | 0 |  | Fixed Annual Cost
Fixed Cost by Capacity |  |  | 72.0715 | /kW-yr |  |  | 70 | $/kW-yr | Fixed Cost by Capacity
Variable Cost by Generation |  |  | 3.992 | /MWh |  |  | 2210000 | $ | User Variable 5 (Annual O&M variable cost)
Fossil Fuel Cost |  |  | 6 | /MMBTU |  |  | 6 | $/MMBTU | Fossil Fual Cost
Estimated O&M labor force |  |  | 40 |  |  |  | 40 |  | Estimated O&M labor force
Note on E9: cturchi: SAM exchange cells must have no $ or % formatting.
Note on E11: cturchi: Equation fits the reference case to match the formula used in DELSOL3. The reference cost is updated to the current project year using the CEPCI.
Note on E12: CST: The reference cost is updated to the current project year using the CEPCI
Note on I25: Craig Turchi: SAM exchange cells must have no $ or % formatting.
Note on E33: Craig Turchi: This value is based on gross turbine output.

## Cap$
NREL Reference Plant Characteristics - southern California | [12 empty] | Labor Cost Factor: | 1 | in use | Based on National Compensation Survey 2011, Natural resources, construction & maintenance workers
|  |  | Variable Name | Cost data Source | [9 empty] | 0.63441 | US national average
Gross Turbine Capacity | 115 | MWe | Ref_Turb_Gross | WP Tower Study, with CA union labor | [9 empty] | 0.47133 | Tucson, AZ
Solar Field Reflector Area | 1289000 | m2 | Ref_SF_area | SAM 2012-11-30 default case area. Cost percentages from Tower Roadmap (SAND2011-2419). Total 2012 cost from industry survey. | [9 empty] | 1 | LA/Riverside, CA (union)
Receiver Thermal Capacity | 910 | MW-t | Ref_Rcvr_MWt | Abengoa GO18149 Report (single tower) | [9 empty] | 0.62664 | LA/Riverside, CA (nonunion)
Receiver Area | 1571 | m2 | Ref_Rcvr_area | Abengoa GO18149 Report (single tower). Receiver area based on Abengoa study design of 20 m dia x 25 m tall cylinder.
Thermal storage capacity | 2790 | MWh-t | Ref_TES_capacity | Abengoa GO18149 Report (one pair tanks)
Annual Net Energy Generation | 590000 | MWh | Ref_Enet_yr | SAM
Land Area | 1018 | acres | Ref_land_area | WP Trough Study (NREL/TP-550-47606), adjusted for limited land grading and smaller blowdown pond
Tower Height | 203 | m | Ref_Tower_height | SAM 2012-11-30 defaults
|  | NREL Reference Plant Data |  |  |  |  | Project Plant Data
ITEM | Reference Year | Size (Basis) | Material Cost | Labor Cost | TOTAL | Size Scaling Exponent | Size (Basis) | Matl cost esc. Factor | Matl cost esc. Rate | Matl cost factor | Material Cost | Labor cost esc. Factor | Labor cost esc. rate | Labor Cost | TOTAL | Category Contingency
DIRECT CAPITAL COSTS
Site - Site Preparation | 2009 | 1018 | 99200 | 164500 | 263700 | 0.9 | 1953 | 10 | 1.214 | 1 | 216469.2159 | 11 | 0.98618 | 291595.7097 | 508064.9256
Site - Clearing & Grubbing | 2009 | 1018 | 0 | 135600 | 135600 | 0.9 | 1953 | 10 | 1.214 | 1 | 0 | 11 | 0.98618 | 240367.041 | 240367.041
Site - Grading, Drainage, Remediation, Retention, & Detention | 2009 | 1018 | 135600 | 878500 | 1014100 | 0.9 | 1953 | 10 | 1.214 | 1 | 295899.4524 | 11 | 0.98618 | 1557245.1732 | 1853144.6256
Site - Evaporation Pond | 2009 | 115 | 370700 | 163400 | 534100 | 0.9 | 115 | 10 | 1.214 | 1 | 450036.8116 | 11 | 0.98618 | 161141.8187 | 611178.6303
Site - Roads, Parking, Fencing | 2009 | 1018 | 5070720 | 3148680 | 8219400 | 0.9 | 1953 | 10 | 1.214 | 1 | 11065068.3708 | 11 | 0.98618 | 5581407.7769 | 16646476.1476
Site - Water Supply Infrastructure | 2009 | 1018 | 359920 | 467720 | 827640 | 0.9 | 1953 | 6 | 1.2182 | 1 | 788082.5578 | 11 | 0.98618 | 829089.0295 | 1617171.5873
|  |  | 6036140 | 4958400 | 10994540 | [5 empty] | 12815556.4084 |  |  | 8660846.549 | 21476402.9574 | 7%
Heliostat Field - Mirrors | 2012 | 1289000 | 44900000 | 0 | 44900000 | 1 | 1289000 | 14 | 1 | 1 | 44900000 | 11 | 1 | 0 | 44900000
Heliostat Field - Drives | 2012 | 1289000 | 80400000 | 0 | 80400000 | 1 | 1289000 | 9 | 1 | 1 | 80400000 | 11 | 1 | 0 | 80400000
Heliostat Field - Pedestal, Mirror Support, Foundation | 2012 | 1289000 | 74200000 | 0 | 74200000 | 1 | 1289000 | 10 | 1 | 1 | 74200000 | 11 | 1 | 0 | 74200000
Heliostat Field - Controls and Wired Connections | 2012 | 1289000 | 7700000 | 0 | 7700000 | 1 | 1289000 | 9 | 1 | 1 | 7700000 | 11 | 1 | 0 | 7700000
Heliostat Field - Field Wiring & Foundations Labor | 2012 | 1289000 | 0 | 13900000 | 13900000 | 1 | 1289000 | 11 | 1 | 1 | 0 | 11 | 1 | 13900000 | 13900000
Heliostat Field - Installation & Checkout | 2012 | 1289000 | 0 | 12400000 | 12400000 | 1 | 1289000 | 11 | 1 | 1 | 0 | 11 | 1 | 12400000 | 12400000
|  |  | 207200000 | 26300000 | 233500000 | [5 empty] | 207200000 |  |  | 26300000 | 233500000 | 7%
Tower - Tower | 2010 | 203 | 12000000 | 9400000 | 21400000 | 0.0113 | 203 | 4 | 1.1199 | 1 | 13439056.3565 | 11 | 0.98178 | 9228753.1355 | 22667809.492
Tower - Riser and Downcomer piping & insulation | 2010 | 203 | 3300000 | 3800000 | 7100000 | 0.0113 | 203 | 8 | 1.0282 | 1 | 3393105.3584 | 11 | 0.98178 | 3730772.5442 | 7123877.9025
|  |  | 15300000 | 13200000 | 28500000 | [5 empty] | 16832161.7149 |  |  | 12959525.6797 | 29791687.3946 | 7%
Receiver - Receiver | 2010 | 1571 | 51500000 | 0 | 51500000 | 0.7 | 1133 | 4 | 1.1199 | 1 | 45880946.1756 | 11 | 0.98178 | 0 | 45880946.1756
Receiver - Horizontal piping & insulation | 2010 | 910 | 9970000 | 10800000 | 20770000 | 0.7 | 670 | 4 | 1.1199 | 1 | 9011686.4932 | 11 | 0.98178 | 8557803.6562 | 17569490.1494
Receiver - Cold Salt Pump(s) | 2010 | 910 | 6880000 | 110000 | 6990000 | 0.7 | 670 | 6 | 1.1241 | 1 | 6241719.1798 | 11 | 0.98178 | 87162.815 | 6328881.9948
Receiver - Controls, Instruments, Heat Trace | 2010 | 910 | 9670000 | 6770000 | 16440000 | 0.7 | 670 | 6 | 1.1241 | 1 | 8772881.4634 | 11 | 0.98178 | 5364475.0697 | 14137356.5331
Receiver - Spare Parts | 2010 | 910 | 1320000 | 0 | 1320000 | 0.7 | 670 | 10 | 1.1233 | 1 | 1196681.8507 | 11 | 0.98178 | 0 | 1196681.8507
|  |  | 79340000 | 17680000 | 97020000 | [5 empty] | 71103915.1626 |  |  | 14009441.5409 | 85113356.7036 | 7%
TES - Cold Tank(s) | 2010 | 2790 | 5810000 | 0 | 5810000 | 0.8 | 2790 | 3 | 1.1013 | 1 | 6398739.226 | 11 | 0.98178 | 0 | 6398739.226
TES - Hot Tank(s) | 2010 | 2790 | 13350000 | 0 | 13350000 | 0.8 | 2790 | 4 | 1.1199 | 1 | 14950950.1966 | 11 | 0.98178 | 0 | 14950950.1966
TES - Media | 2010 | 2790 | 43170000 | 0 | 43170000 | 1 | 2790 | 21 | 1 | 1 | 43170000 | 11 | 0.98178 | 0 | 43170000
TES - Piping, Insulation, Valves, & Fittings | 2010 | 2790 | 1790000 | 3170000 | 4960000 | 0.8 | 2790 | 6 | 1.1241 | 1 | 2012080.8653 | 11 | 0.98178 | 3112249.7276 | 5124330.5929
TES - Foundations & Support Structures | 2010 | 2790 | 2790000 | 2620000 | 5410000 | 0.8 | 2790 | 10 | 1.1233 | 1 | 3133903.2819 | 11 | 0.98178 | 2572269.491 | 5706172.7729
TES - Instrumentation & Controls | 2010 | 2790 | 420000 | 480000 | 900000 | 0.8 | 2790 | 7 | 1.0159 | 1 | 426681.9312 | 11 | 0.98178 | 471255.4793 | 897937.4105
|  |  | 67330000 | 6270000 | 73600000 | [5 empty] | 70092355.5011 |  |  | 6155774.6978 | 76248130.1989 | 7%
Fossil Backup | 2012 | 115 | 0 | 0 | 0 | 0.8 | 115 | 3 | 1 | 1 | 0 | 11 | 1 | 0 | 0 | 7%
SAM BOP defined as Steam Generation System
BOP - Steam Generation Heat Exchangers and Equipment | 2012 | 115 | 7300000 | 100000 | 7400000 | 0.8 | 115 | 4 | 1 | 1 | 7300000 | 11 | 1 | 100000 | 7400000
BOP - Hot Salt Pump(s) | 2012 | 115 | 3010000 | 190000 | 3200000 | 0.8 | 115 | 8 | 1 | 1 | 3010000 | 11 | 1 | 190000 | 3200000
BOP - Steam Piping, Insulation, Valves, & Fittings | 2012 | 115 | 1200000 | 970000 | 2170000 | 0.8 | 115 | 6 | 1 | 1 | 1200000 | 11 | 1 | 970000 | 2170000
BOP - Electrical, Instrumentation, and Controls System | 2012 | 115 | 3900000 | 6700000 | 10600000 | 0.8 | 115 | 7 | 1 | 1 | 3900000 | 11 | 1 | 6700000 | 10600000
BOP - Foundations & Support Structures | 2012 | 115 | 9600000 | 7800000 | 17400000 | 0.8 | 115 | 10 | 1 | 1 | 9600000 | 11 | 1 | 7800000 | 17400000
|  |  | 25010000 | 15760000 | 40770000 | [5 empty] | 25010000 |  |  | 15760000 | 40770000 | 7%
Power Plant - Steam Turbine Generator Island | 2012 | 115 | 21160000 | 5020000 | 26180000 | 0.8 | 115 | 5 | 1 | 1 | 21160000 | 11 | 1 | 5020000 | 26180000
Power Plant - Blowdown System | 2012 | 115 | 134000 | 110000 | 244000 | 0.8 | 115 | 8 | 1 | 1 | 134000 | 11 | 1 | 110000 | 244000
Power Plant - Cooling Systems | 2012 | 115 | 15600000 | 7930000 | 23530000 | 0.8 | 115 | 3 | 1 | 1 | 15600000 | 11 | 1 | 7930000 | 23530000
Power Plant - Condensate System | 2012 | 115 | 680000 | 690000 | 1370000 | 0.8 | 115 | 6 | 1 | 1 | 680000 | 11 | 1 | 690000 | 1370000
Power Plant - Feedwater System | 2012 | 115 | 5220000 | 2410000 | 7630000 | 0.8 | 115 | 8 | 1 | 1 | 5220000 | 11 | 1 | 2410000 | 7630000
Power Plant - Auxiliary Cooling Water System | 2012 | 115 | 1600000 | 1330000 | 2930000 | 0.8 | 115 | 6 | 1 | 1 | 1600000 | 11 | 1 | 1330000 | 2930000
Power Plant - Steam Piping, Insulation, Valves, & Fittings | 2012 | 115 | 4250000 | 3830000 | 8080000 | 0.8 | 115 | 6 | 1 | 1 | 4250000 | 11 | 1 | 3830000 | 8080000
Power Plant - Fuel Gas Handling & Metering System | 2012 | 115 | 0 | 0 | 0 | 0.8 | 115 | 6 | 1 | 1 | 0 | 11 | 1 | 0 | 0
Power Plant - Water Treatment System | 2012 | 115 | 2530000 | 1310000 | 3840000 | 0.8 | 115 | 3 | 1 | 1 | 2530000 | 11 | 1 | 1310000 | 3840000
Power Plant - Power Distribution Systems | 2012 | 115 | 13350000 | 2340000 | 15690000 | 0.8 | 115 | 9 | 1 | 1 | 13350000 | 11 | 1 | 2340000 | 15690000
Power Plant - Back-up Power Systems | 2012 | 115 | 2330000 | 410000 | 2740000 | 0.8 | 115 | 9 | 1 | 1 | 2330000 | 11 | 1 | 410000 | 2740000
Power Plant - Instruments and Controls System | 2012 | 115 | 2700000 | 2140000 | 4840000 | 0.8 | 115 | 7 | 1 | 1 | 2700000 | 11 | 1 | 2140000 | 4840000
Power Plant - Fire Protection System | 2012 | 115 | 2190000 | 1090000 | 3280000 | 0.8 | 115 | 4 | 1 | 1 | 2190000 | 11 | 1 | 1090000 | 3280000
Power Plant - Foundations & Support Structures | 2012 | 115 | 2300000 | 5300000 | 7600000 | 0.8 | 115 | 10 | 1 | 1 | 2300000 | 11 | 1 | 5300000 | 7600000
Power Plant - Buildings | 2012 | 115 | 7280000 | 2740000 | 10020000 | 0.8 | 115 | 12 | 1 | 1 | 7280000 | 11 | 1 | 2740000 | 10020000
Power Plant - BOP Mechanical Systems | 2012 | 115 | 2656000 | 2550000 | 5206000 | 0.8 | 115 | 4 | 1 | 1 | 2656000 | 11 | 1 | 2550000 | 5206000
Power Plant - BOP Electrical Systems | 2012 | 115 | 2710000 | 12160000 | 14870000 | 0.8 | 115 | 9 | 1 | 1 | 2710000 | 11 | 1 | 12160000 | 14870000
|  |  | 86690000 | 51360000 | 138050000 | [5 empty] | 86690000 |  |  | 51360000 | 138050000 | 7%
Direct Capital Cost Subtotal |  |  | 486906140 | 135528400 | 622434540 |  | Direct Capital Cost Subtotal |  |  |  | 489743988.787 |  |  | 135205588.4674 | 624949577.2545
Contingency (total) |  |  |  |  | 43570000 |  | Contingency (total) | [7 empty] | 43746470.4078
Contingency (% of Direct Capital Costs) |  |  |  | 7% |  |  | Contingency (% of Direct Capital Costs) | [7 empty] | 7%
Direct Capital Costs Total |  |  |  |  | 666004540 |  | Direct Capital Costs Total | [7 empty] | 668696047.6623
INDIRECT PROJECT COSTS |  | Size (Basis) | % of Basis | Fixed Value |  |  | INDIRECT PROJECT COSTS
EPC and OWNER COSTS: | [6 empty] | Size (Basis)
Engineering (EPCM basis) | 2012 | 666004540 | 2.2% | 0 | 14652099.88 | 0.9 | 668696047.6623 |  |  |  |  | 13 | 1 |  | 14705380.9793
Construction management (EPCM basis) | 2012 | 666004540 | 1.6% | 0 | 10656072.64 | 0.9 | 668696047.6623 |  |  |  |  | 13 | 1 |  | 10694822.5304
Commissioning / start-up (EPCM basis) | 2012 | 666004540 | 0.2% | 0 | 1332009.08 | 0.9 | 668696047.6623 |  |  |  |  | 13 | 1 |  | 1336852.8163
Owner's Engg & Project Mgmt | 2012 | 666004540 | 4% | 0 | 26640181.6 | 0.9 | 668696047.6623 |  |  |  |  | 13 | 1 |  | 26737056.326
Permitting, Licensing, Legal | 2012 | 666004540 | 3% | 0 | 19980136.2 | 0.9 | 668696047.6623 |  |  |  |  | 13 | 1 |  | 20052792.2445
EPC Costs Subtotal |  |  |  |  | 73260499.4 |  | EPC Costs Subtotal | [7 empty] | 73526904.8964
LAND
Land (acres) | 2009 | 1018 | 10000 | per acre | 10180000 |  | 1953 |  |  |  | 10000 | per acre |  |  | 19530000
OTHER COSTS: | [6 empty] | OTHER COSTS:
Builder's All Risk Insurance |  |  |  |  | #REF! |  | Builder's All Risk Insurance | [7 empty] | #REF!
Worker's Compensation & Employers' Liability |  |  |  |  | #REF! |  | Worker's Compensation & Employers' Liability | [7 empty] | #REF!
Commercial General Liability |  |  |  |  | #REF! |  | Commercial General Liability | [7 empty] | #REF!
Payment & Performance Bond |  |  |  |  | #REF! |  | Payment & Performance Bond | [7 empty] | #REF!
Owner's Cost |  |  |  |  | #REF! |  | Owner's Cost | [7 empty] | #REF!
Indir Startup Spares |  |  |  |  | #REF! |  | Indir Startup Spares | [7 empty] | #REF!
Contractor's Engineering |  |  |  |  | #REF! |  | Contractor's Engineering | [7 empty] | #REF!
Escalation |  |  |  |  | #REF! |  | Escalation | [7 empty] | #REF!
Project, Land, Misc. |  |  |  |  | #REF! |  | Project, Land, Misc. | [7 empty] | #REF!
%DC's Sales Tax Applies |  |  |  |  | #REF! |  | %DC's Sales Tax Applies | [7 empty] | #REF!
Legal Expenses |  |  |  |  | #REF! |  | Legal Expenses | [7 empty] | #REF!
Warranty |  |  |  |  | #REF! |  | Warranty | [7 empty] | #REF!
Permits & Fees |  |  |  |  | #REF! |  | Permits & Fees | [7 empty] | #REF!
Other Costs Subtotal |  |  |  |  | #REF! |  | Other Costs Subtotal | [7 empty] | #REF!
Land Costs Subtotal |  |  |  |  | 10180000 |  | Project, Land, Misc Costs Subtotal | [7 empty] | 19530000
SALES TAX | [6 empty] | SALES TAX
Tax Rate (input from SAM) | 5% | [5 empty] | Tax Rate (input on SAM Exchange sheet) |  |  |  |  | 5%
Tax Basis (Direct Capital Material Costs incl Contingency) |  | 520989569.8 |  |  |  |  | Tax Basis (Direct Capital Material Costs incl Contingency) | [6 empty] | 524026068.0021
Basis percentage of Total Direct Costs incl Contingency |  |  | 78.23% |  |  |  | Basis percentage of Total Direct Costs incl Contingency | [6 empty] | 78.37%
Sales Tax Cost Subtotal |  |  |  |  | 26049478.49 |  | Sales Tax Cost Subtotal | [7 empty] | 26201303.4001
Note on F13: Craig Turchi: Reference Plant is based on California union wage rates.
Note on I13: Craig Turchi: Project Plant costs are calculated by: (Ref Plant Cost) * (Proj Plant Size / Ref Plant Size)^(scaling exponent)
Note on K13: Craig Turchi: Enter number corresponding to the desired Cost index Factor Num. on sheet CI
Note on M13: Craig Turchi: Cost factors allow the user to adjust material costs without changing the spreadsheet formula, for example to simulate a new technology
Note on O13: Craig Turchi: Enter number corresponding to the desired Cost index Factor Num. on sheet CI
Note on B15: cturchi: Assume amount of clearing/grading only 10% of that for a trough plant.
Note on B16: cturchi: Assume amount of clearing only 10% of that for a trough plant.
Note on B17: cturchi: Assume amount of grading only 10% of that for a trough plant.
Note on E23: CST: Heliostat Field costs use $/m2 from SAND2011-2419 times 1.2 multiplier for "manu facilities and profit" from the reference.
Note on I31: cturchi: Scales as an exponential: Cost = RefCost*exp(Height*0.0113) as per DELSOL3
Note on I32: cturchi: Scales as an exponential: Cost = RefCost*exp(Height*0.0113) as per DELSOL3
Note on B86: cturchi: These values set to give total Indirect Cost of 11% of Direct Costs. Individual percentages not based on any reference.

## O&M$
Reference Plant Characteristics - see Cap$ sheet |  |  | Variable Name | [7 empty] | Labor Cost Factor: | see Cap$ cell Q1
Labor Burden Rate | 35% |  | DL_burden
O&M Labor requirements based on Parabolic Trough Study, NREL/TP-550-47605
| Reference Plant Data | [6 empty] | Project Plant Data
ITEM | Reference Year | Size (Basis) | Qty | Annual Salary California Location ($/yr) | Burdened Labor Cost |  | Size Scaling Exponent | Size | Labor cost esc. Factor | Labor cost esc. rate | Cost factor | Burdened Labor Cost | Workers
Admininstration Labor
Admin - Plant Manager | 2011 | 1289000 | 1 | 194000 | 261900 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 258695.527 | 1
Admin - Administrative Aide | 2011 | 1289000 | 1 | 70000 | 94500 |  | 0 | 1289000 | 11 | 0.98628 | 1 | 93203.5024 | 1
Admin - Financial Manager | 2011 | 1289000 | 1 | 184000 | 248400 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 245360.706 | 1
Admin - Purchasing | 2011 | 1289000 | 1 | 108000 | 145800 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 144016.0666 | 1
Admin - Human Resources | 2011 | 1289000 | 1 | 110000 | 148500 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 146683.0308 | 1
Admin - Plant Engineer | 2011 | 1289000 | 1 | 191000 | 257850 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 254695.0807 | 1
Admin - Performance Engineer | 2011 | 1289000 | 1 | 135000 | 182250 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 180020.0832 | 1
Admin - Information Technology | 2011 | 1289000 | 1 | 178000 | 240300 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 237359.8135 | 1
Admin - Clerk | 2011 | 1289000 | 0 | 70000 | 0 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 0 | 0
Admin - | 2011 | 1289000 | 0 | 0 | 0 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 0 | 0
|  |  | 8 |  | 1579500 | [6 empty] | 1560033.8103 | 8
Operations Labor
Ops - Operations Manager | 2011 | 1289000 | 1 | 129000 | 174150 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 172019.1907 | 1
Ops - Asst Ops Manager | 2011 | 1289000 | 0 | 129000 | 0 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 0 | 0
Ops - Control Room Operator | 2011 | 1289000 | 4 | 103000 | 556200 |  | 0 | 1289000 | 11 | 0.98628 | 1 | 548569.1857 | 4
Ops - Plant Equipment Operator, Technician | 2011 | 1289000 | 2 | 97000 | 261900 |  | 1 | 1289000 | 11 | 0.98628 | 1 | 258306.8496 | 2
Ops - Asst Plant Equipment Operator | 2011 | 1289000 | 4 | 65000 | 351000 |  | 1 | 1289000 | 11 | 0.98628 | 1 | 346184.4376 | 4
Ops - | 2011 | 1289000 | 0 | 0 | 0 |  | 1 | 1289000 | 11 | 0.98628 | 1 | 0 | 0
Ops - | 2011 | 1289000 | 0 | 0 | 0 |  | 1 | 1289000 | 11 | 0.98628 | 1 | 0 | 0
|  |  | 11 |  | 1343250 | [6 empty] | 1325079.6636 | 11
Power Block / TES Maintenance Labor
PB - Maintenance Supervisor | 2011 | 115 | 1 | 124000 | 167400 |  | 0 | 115 | 13 | 0.98776 | 1 | 165351.7802 | 1
PB - Maintenance Foreman | 2011 | 115 | 1 | 124000 | 167400 |  | 0 | 115 | 13 | 0.98776 | 1 | 165351.7802 | 1
PB - Electrician | 2011 | 115 | 1 | 106000 | 143100 |  | 0.7 | 115 | 11 | 0.98628 | 1 | 141136.7323 | 1
PB - Instrument Technician | 2011 | 115 | 2 | 97000 | 261900 |  | 0.7 | 115 | 11 | 0.98628 | 1 | 258306.8496 | 2
PB - Machinist/Welder/Mechanical Technician | 2011 | 115 | 2 | 97000 | 261900 |  | 0.7 | 115 | 11 | 0.98628 | 1 | 258306.8496 | 2
PB - Clerk/Assistant | 2011 | 115 | 4 | 65000 | 351000 |  | 0.7 | 115 | 11 | 0.98628 | 1 | 346184.4376 | 4
PB - | 2011 | 115 | 0 | 0 | 0 |  | 0.7 | 115 | 11 | 0.98628 | 1 | 0 | 0
PB - | 2011 | 115 | 0 | 0 | 0 |  | 0.7 | 115 | 11 | 0.98628 | 1 | 0 | 0
|  |  | 11 |  | 1352700 | [6 empty] | 1334638.4294 | 11
Solar Field Maintenance Labor
SF - Maintenance Supervisor | 2011 | 1289000 | 1 | 124000 | 167400 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 165351.7802 | 1
SF - Maintenance Foreman | 2011 | 1289000 | 1 | 124000 | 167400 |  | 0 | 1289000 | 13 | 0.98776 | 1 | 165351.7802 | 1
SF - Instrument Technician | 2011 | 1289000 | 2 | 97000 | 261900 |  | 0.7 | 1289000 | 11 | 0.98628 | 1 | 258306.8496 | 2
SF - Machinist/Welder/Mechanical Technician | 2011 | 1289000 | 2 | 97000 | 261900 |  | 0.7 | 1289000 | 11 | 0.98628 | 1 | 258306.8496 | 2
SF - Clerk/Assistant | 2011 | 1289000 | 4 | 65000 | 351000 |  | 0.7 | 1289000 | 11 | 0.98628 | 1 | 346184.4376 | 4
SF - | 2011 | 1289000 | 0 | 0 | 0 |  | 1 | 1289000 | 11 | 0.98628 | 1 | 0 | 0
SF - | 2011 | 1289000 | 0 | 0 | 0 |  | 1 | 1289000 | 11 | 0.98628 | 1 | 0 | 0
|  |  | 10 |  | 1209600 | [6 empty] | 1193501.6971 | 10
Labor Subtotal |  |  | 40 |  | 5485050 | [6 empty] | 5413253.6004 | 40
| Reference Year | Size (Basis) | Units/yr | Rate ($/unit) | Cost |  |  | Size | Cost esc. Factor | Cost esc. rate | Cost factor | Cost
Service Contracts
SCon - Control Systems | 2009 | 1 | 1 | 100000 | 100000 |  | 1 | 1 | 11 | 0.98618 | 1 | 98618.0041
SCon - Computers/Office Equipment | 2009 | 40 | 1 | 105000 | 105000 |  | 1 | 40 | 11 | 0.98618 | 1 | 103548.9043
SCon - Grounds/house keeping | 2009 | 1289000 | 1 | 100000 | 100000 |  | 0.5 | 1289000 | 11 | 0.98618 | 1 | 98618.0041
SCon - Mirror washing | 2009 | 1289000 | 1 | 350000 | 350000 |  | 1 | 1289000 | 30 | 1 | 1 | 350000
SCon - Water Treatment | 2009 | 115 | 1 | 145000 | 145000 |  | 1 | 115 | 30 | 1 | 1 | 145000
SCon - | 2009 | 1 | 0 |  | 0 |  | 1 | 1 | 30 | 1 | 1 | 0
[5 empty] | 800000 | [6 empty] | 795784.9126
Utilities
Util - Natural Gas (MMBTU) | 2009 | 115 | 0 | 6 | 0 |  | 1 | 115 | 30 | 1 | 1 | 0
Util - Water (acre/ft) | 2009 | 115 | 124.1 | 450 | 55845 |  | 1 | 115 | 30 | 1 | 1 | 55845
Util - Auxiliary Power (MWh) | 2009 | 115 | 3703 | 80 | 296240 |  | 1 | 115 | 30 | 1 | 1 | 296240
[5 empty] | 352085 | [6 empty] | 352085
| Reference Year | Size (Basis) | Fraction of Cost basis | Ref Plant Cost Basis | Cost |  |  | Size | Cost esc. Factor | Cost esc. rate | Cost factor | Cost
Materials & Maintenance (% of Capital Cost Basis)
Misc - Site | 2009 | 1289000 | 0.003 | 10994540 | 32983.62 |  | 1 | 1289000 | 30 | 1 | 1 | 32983.62
Misc - Solar Field | 2009 | 1289000 | 0.003 | 233500000 | 700500 |  | 1 | 1289000 | 30 | 1 | 1 | 700500
Misc - Receiver | 2009 | 910 | 0.003 | 97020000 | 291060 |  | 1 | 670 | 30 | 1 | 1 | 214296.9231
Misc - TES | 2009 | 2790 | 0.003 | 73600000 | 220800 |  | 0.7 | 10 | 30 | 1 | 1 | 4286.2365
Misc - Fossil Backup | 2009 | 115 | 0.01 | 0 | 0 |  | 0.7 | 115 | 30 | 1 | 1 | 0
Misc - Powerblock | 2009 | 115 | 0.02 | 138050000 | 2761000 |  | 0.7 | 115 | 30 | 1 | 1 | 2761000
[5 empty] | 4006343.62 | [6 empty] | 3713066.7795
Annual O&M Summary (Reference) | [7 empty] | Annual O&M Summary (Project)
Burdened Labor |  |  |  |  | 5485050 | fixed |  | Burdened Labor |  |  |  | 5413253.6004
Service Contracts |  |  |  |  | 800000 | fixed |  | Service Contracts |  |  |  | 795784.9126
Utilities |  |  |  |  | 352085 | variable |  | Utilities |  |  |  | 352085
Materials & Misc |  |  |  |  | 4006343.62 | var/fixed |  | Materials & Misc |  |  |  | 3713066.7795
[5 empty] | 10643478.62 | [6 empty] | 10274190.2925
|  |  |  | Fixed Cost by Capacity ($/kW-yr) | 72.0715 |  |  |  |  | Fixed Cost by Capacity ($/kW-yr) |  | 70.1354
|  |  |  | Variable Cost by Generation ($/MWh) | 3.992 |  |  |  |  | Annual Variable Cost ($) |  | 2208618.3898
Note on F6: Craig Turchi: Reference salaries based on national means from US Bureau of Labor under NAICS 221100, Electric Power Generation, Transmission and Distribution, May 2011. National means adjusted up to California Reference plant location by ratio.
Note on I6: Craig Turchi: Project Plant costs are calculated by: (Ref Plant Cost) * (Proj Plant Size / Ref Plant Size)^(scaling exponent)
Note on M6: Craig Turchi: Cost factors allow the user to adjust project costs without changing the spreadsheet formula.
Note on M51: Craig Turchi: Cost factors allow the user to adjust project costs without changing the spreadsheet formula.
Note on M66: Craig Turchi: Cost factors allow the user to adjust project costs without changing the spreadsheet formula.

## CI
Cost Index Sheet
Data Source: | [12 empty] | Data Source: | [6 empty] | User Defined
Chemical Engineering Plant Cost Index (CEPCI) | [12 empty] | Producer Price Index (PPI)
http://www.che.com/ | [12 empty] | http://www.bls.gov/ppi/
Factor Num = | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Period | CE INDEX | Equipment | Heat Exchangers and Tanks | Process Machinery | Pipe, valves and fittings | Process Instruments | Pumps and Compressors | Electrical equipment | Structural supports | Construction Labor | Buildings | Engineering Supervision | PPI WPU1311 Flat Glass | PPI WPU06520135 Syn NH3 | PPI WPU06140197 Aromatic Chems |  |  |  |  | Solar Salt ($/MT) | [8 empty] | None
1998 | 389.5 | 436 | 382.8 | 430.8 | 534.8 | 365.3 | 648.5 | 333.6 | 394.3 | 287.4 | 374.2 | 341.2 | 107.1 | [15 empty] | 1
1999 | 390.6 | 435.5 | 371.2 | 433.6 | 531.6 | 363.5 | 658.4 | 335.8 | 413.1 | 292.5 | 380.2 | 339.9 | 106.4 | [15 empty] | 1
2000 | 394.1 | 438 | 370.6 | 439.4 | 545.9 | 368.5 | 665.3 | 339.4 | 408.7 | 299.2 | 385.6 | 340.6 | 109.7 | [15 empty] | 1
2001 | 394.3 | 437.3 | 363.9 | 439.5 | 548.1 | 362.9 | 683.2 | 341.2 | 413.9 | 302.3 | 385.6 | 341.5 | 112 | [6 empty] | 400 | [8 empty] | 1
2002 | 395.6 | 437.5167 | 356.925 | 444.15 | 555.8417 | 363.5083 | 699.1917 | 341.3583 | 415.45 | 305.7917 | 390.4167 | 345.3333 | 111.2417 |  | 100.3 |  |  |  |  | 520 | [8 empty] | 1
2003 | 402.0833 | 445.475 | 363.5333 | 451.5417 | 570.8 | 365.3833 | 705.3083 | 341.5833 | 428.4833 | 308.8167 | 400.1667 | 347.4167 | 110.975 | 101.0429 | 126 |  |  |  |  | 650 | [8 empty] | 1
2004 | 444.225 | 508.125 | 464.825 | 490.9833 | 600.625 | 374.3333 | 719.4333 | 351.0167 | 537.4833 | 307.7333 | 428.5667 | 345.1833 | 108.5833 | 115.05 | 181.4 |  |  |  |  | 780 | [8 empty] | 1
2005 | 468.1667 | 543.675 | 513.9333 | 519.65 | 623.7 | 381.825 | 752.5 | 372.1417 | 584.7667 | 305.55 | 445.1 | 346.7917 | 110.9833 | 132.2167 | 224.2 |  |  |  |  | 900 | [8 empty] | 1
2006 | 499.55 | 588.0417 | 547.95 | 549.7083 | 708.0083 | 420.125 | 785.7333 | 403.0667 | 625.3 | 309.3167 | 468.5667 | 350.925 | 113.4583 | 139.5583 | 272.5 |  |  |  |  | 1020 | [8 empty] | 1
2007 | 525.4167 | 624.3583 | 592.1083 | 598.2667 | 733.6 | 425.25 | 831.175 | 430.4667 | 662.6167 | 315.125 | 476.775 | 357.0083 | 114.1667 | 156 | 287.3 |  |  |  |  | 1150 | [8 empty] | 1
2008 | 575.4 | 696.8 | 687.6 | 643.4 | 827.6 | 434.6 | 871.7 | 458.5 | 748.6 | 321.7 | 506.9 | 352.9 | 115.9 | 240.3 | 323.7 |  |  |  |  | 1300 | [8 empty] | 1
2009 | 521.925 | 615.675 | 558.325 | 598.55 | 760.7333 | 397.4667 | 897.2667 | 461.525 | 629.15 | 327.425 | 492.0333 | 346.85 | 115 | 169 | 251.9 |  |  |  |  | 1080 | [8 empty] | 1
2010 | 550.8083 | 659.3833 | 610.4 | 622.4917 | 824.4167 | 422.1833 | 902.6333 | 478.7167 | 679.9833 | 328.8917 | 504.325 | 339.0583 | 111.2 | 171.4 | 331.3 |  |  |  |  | 1200 | [8 empty] | 1
2011 | 585.9833 | 713.2917 | 675.8667 | 666.6917 | 889.1667 | 437.8083 | 903.6417 | 506.2583 | 754.9917 | 327.3917 | 517.1333 | 332.3667 | 112.8 | 237.1 | 432.3 |  |  |  |  | 1200 | [8 empty] | 1
2012 | 593.8 | 726.2 | 683.6 | 680.1 | 926.7 | 428.9 | 928.1 | 515.2 | 763.8 | 322.9 | 527.7 | 328.3 | 113.9 | 254.2 | 415.6 |  |  |  |  | 1200 | [8 empty] | 1
2013 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2014 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2015 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2016 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2017 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2018 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2019 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x |  |  |  |  | x | [8 empty] | 1
2020 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | [13 empty] | 1
Note on U6: Craig Turchi: NREL estimate from industry sources in $ per metric tonne.
Note on A21: CST: Values for May/June 2012 used for annual